**Section 653.606 Exemptions From Chlorination - Satellite Supplies**

a) Satellite community water supplies are exempt from chlorination provided the requirements of Section 653.604 are met.

b) Chlorination facilities shall be installed and used:

1) whenever the chlorine residual in any active part of the distribution system drops below 0.2 mg/l free or 0.5 mg/l combined; or

2) if daily operating report records of chlorine residuals are not kept and submitted to the Agency.